Citect for Windows

Driver Specification

Novatune/Novabas SLPD Driver

| Author: | Tomas Rook |
| --- | --- |
| Date: Rev: Rev: Rev: Rev: Rev: Rev: Rev: | 14/01/99 02/01/00 30/08/01 10/12/01 15/02/01 05/10/04 23/11/06 16/09/14 |

Contents

1.	QA	5

1.1	Introduction	5

1.2	Procedure for generating a new driver	5

2.	Target Device(s) and Protocol	6

2.1	Introduction	6

2.2	Device Manufacturer	6

2.3	Device Definition	6

2.4	Communications Method	6

2.5	Communications/Hardware Configuration	6

2.5.1	I/O Device Settings	7

2.6	Contacts	7

3.	Protocol Requirements	8

3.1	Introduction	8

3.2	Initialising the Port	8

3.3	IO Device Online Test	8

3.4	Message Structure	8

3.5	Data Format	9

3.6	Break	9

3.7	Pause	9

3.8	Checksum	9

3.9	Extended Protocol Description	9

3.10	Error Handling	9

4.	General Driver description	10

4.1	Cache	10

4.2	Cyclic update vs. Cache reads	10

4.3	First time reads	10

4.4	Request Performance	10

4.5	SLPD Performance	10

4.6	Writes	11

4.7	Citect Cache	11

4.8	System Device	11

4.9	NOVATUNE.DBF	11

5.	User Interface	12

5.1	Introduction	12

5.2	Driver Name	12

5.3	Ports Form	12

5.3.1	Baud Rate	12

5.3.2	Data Bits	12

5.3.3	Stop Bits	12

5.3.4	Parity	12

5.3.5	Special Opt	12

5.4	IO Devices Form	12

5.4.1	Protocol	12

5.4.2	Address	12

5.5	Pulldown lists Help	12

5.6	IO Device Data Types and Formats	13

5.7	IO Device Function Blocks and their Parameters (NOVATUNE.DBF)	13

5.8	PROTDIR.DBF	17

5.9	Parameters and INI options	17

5.9.1	Standard Parameters	17

5.9.2	Driver Specific Parameters	17

5.10	Driver Specific Errors	19

5.11	Driver Error Help	20

5.12	Debug Messages	20

5.13	Stats Special Counters	20

5.14	Program up/download	21

5.15	Hints and Tips	23

6.	Basic Testing	25

6.1	Introduction	25

6.2	Procedure	25

7.	Performance Testing	27

7.1	Introduction	27

7.2	Calculating the Blocking Constant – Not applicable	27

8.	References	28

8.1	References	28

# QA

## Introduction

This document follows the development of the new driver. It serves as a functional specification, design specification and test specification.

## Procedure for generating a new driver

The following check list defines the QA steps for generating a new driver. This procedure must be followed for drivers to be integrated into Citect.

|  | Description | Person | Date |
| --- | --- | --- | --- |
| 1 | This specification document is written. | TR | 99.02.25 |
| 2 | Specification reviewed and accepted by R&D department. |  |  |
| 3 | Driver coded. | TR | 98.11.05 |
| 4 | Code and specification reviewed and accepted by R&D department. |  |  |
| 5 | Testing with connection project, and performance test. | TR | 99.02.16 |
| 6 | Driver integrated into Citect source and built. |  |  |
| 7 | Documentation is written (HLP or MVB files) |  |  |
|  | At this checkpoint coding is done and the driver is available as a beta. |  |  |
| 8a | Full testing is carried out. | TR | 99.05.18 |
| 8b | Performance testing is carried out. | TR | 99.05.18 |
| 8c | Specification and documentation updated from testing/performance tests | TR | 99.05.18 |
|  | At this checkpoint the testing is complete. |  |  |
| 9a | Review for completeness by developer, tester, documentor and R&D staff |  |  |
| 9b | Add driver to install disks |  |  |
| 9c | Add driver to protocols database |  |  |
| 9d | Support notified of new driver for training purposes |  |  |
| 10 | Sales notified of new driver |  |  |
|  | The driver is now finished. |  |  |

The hand over of a driver requires that all the above steps are completed and checked off.

# Target Device(s) and Protocol

## Introduction

This section defines the types of I/O Devices that are targeted by this driver.

## Device Manufacturer

ABB Automation AB
Sickla Allé 13
120 86  STOCKHOLM
SWEDEN

Phn: +46 8 658 81 00

## Device Definition

Novatune 800
Novabas 100

These devices are the digital substations (DSS) that ABB and their partners configurate and program for different building automation projects. They have a configurable number of I/O’s (digital input, analog input, analog output etc).

## Communications Method

Serial RS-422, multidrop. The driver act as the master.

## Communications/Hardware Configuration

The PC is conected to the devices using a standard RS-232/RS-422 converter, RS-422 digiboard or similar equipment. The devices are polled from the PC and responds with data. When the devices not are in transmitting mode, their RS-422 driver is set to 'high impedance', making it possible to connect several devices at one bus. Therefore, it is very important that the bus is properly terminated, especially the TX line from the devices which has to be terminated at both ends.

To be assured that the correct levels are received when the RS-422 drivers are in high impedance mode, the TX line from the devices should be pulled up/down by a weak current. This is supported by some converters. If not, a weak pull up/down resistor should be used, i.e. 2,2k to +5 VDC or 4,7k to +12VDC and 1k to GND.

Be careful when selecting hardware, though ethernet based terminal servers using COM-port emulating software (Digi Etherlite for example) does not implement the break/pause function thoroughly and will not work correctly.

The PC must be connected at the end of the bus.

If the cable length is to exceed 1200 m (AWG24), a RS-422 repeater has to be used. 

The Novabas devices uses 24 VAC, 50 Hz, and the Novatune devices 240 VAC, 50 Hz.

### Ethernet and UDP/IP possibilities

There is a version of the Westermo ED-10 available that have the SLPD specific break handling implemented.

The driver communicates using UDP/IP over ethernet to the Westermo ED-10, wich in turn use RS-422 for the local connected devices. The configuration is suitable to improve performance.

### I/O Device Settings

The driver supports any baud rate available by the devices, so the previous settings could be used, but at least 4800 bps is preferred. The device response time is about 250 ms at 4800 bps, and is increasing to about 800 ms at 1200 bps (a message with 16 channels).

## Contacts

Driver Development	TroSoft, Tomas Rook	+46 8 532 57262
SLPD reference	OrbiTec AB, Kay Persson	+46 36 162870
Project Managment	PiiGAB, Bertil Göransson	+46 31 559977

# Protocol Requirements

## Introduction

This section documents all the requirements of the protocol itself.

## Initialising the Port

No special initialisation is necessary.

## IO Device Online Test

The drivers’ response to CTDRV_INIT_UNIT and CTDRV_STATUS_UNIT is to issue a PDSW (PD Status Word) read from the device The PDSW read returns the status, i.e. Normal, Remote Program, Local Program or Local mode. If the PDSW read is successful, it is immediately followed by a Normalise Command to assure that the device will report any events. This will also cause the device to reset its read and write sequence flags. If the normalise was ok, it will be followed by a clock write. This could be turned off by a parameter in CITECT.INI.

## Message Structure

The message structure has the following formats :

Driver requests (master):

| Break | Preamble | Preamble | Address | Function | Length | Data | LRC | Postamble |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Valid reponses (slaves):

| Preamble | Address | Function | Length | LRC | Postamble |
| --- | --- | --- | --- | --- | --- |

or

| Preamble | Address | Function | Length | B | B | Fi | Data | LRC | Postamble |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

The messages may be up to 41 bytes wide.

| Break | Transmits a break state at the line |
| --- | --- |
| Preamble | 0x00 |
| Address | 0x00-0xFE (0xFF is reserved for broadcasts) |
| Function | Function Code (see SLPD driver specification) |
| Length | Lengthcode for the data field |
| B | The first channel that is returned in the data field (the first B is always 0x00, channels span from 0x00 - 0xFF) |
| Fi | Number of channels that is returned in data field |
| Data | Data field, max 35 bytes |
| LRC | Linear Redundancy Check |
| Postamble | 0x00 |

## Data Format

The data format is 8-bit binary. Any character from 0x00 - 0xFF is valid in the data part.

## Break

To set the devices in a listening state, the driver transmits a break state at the line. The default break time is 40 bits, and is calculated by the driver. If no baudrate is reported by Citect, the driver assumes that it is 1200 bps, and sets the break time to 33 ms.

Break is only sent by the master.

## Pause

When the break time has passed and the line is back in normal state, a pause must be made before the first preamble is sent. The default pause time is 40 bits, and is calculated by the driver. If no baudrate is reported by Citect, the driver assumes that it is 1200 bps, and sets the pause time to 33 ms.

If UDP/IP is used, the receiving device must provide the break signal and pause! TCP/IP is not supported by the driver.

## Checksum

The LRC is calculated by XORing the bytes in the message. The Break and preambles/postambles are not included.

## Extended Protocol Description

The fully protocol description is found in the IL-SPEC-7159/0, document 5766 398-19, available from ABB Automation.

## Error Handling

3 consecutive timeouts at read or write requests will put the device off-line (defaulted to 2 retries). However, if the device is polled i.e. the event queue is checked (described below) then it has to fail for 6 consecutive times before the device is put off-line.

Example: If there is three devices, which are all polled, the driver will poll them in a round queue order fashion (poll loop). If device two fails or is disconnected, then the driver will not suceed to poll the event queue, but the driver will continue and do the next poll at device three, not reporting any error, and not do any retries. Then the driver will begin with device one again. When device two has failed to respond for six poll loops, it will be put off-line. This means that the time before the device is put off-line is dependant of the number of devices at the bus. If there is only one device at the bus, the time will be about 15 seconds. If there are five devices at the bus, the fail time will be about 30 seconds.

The device will return to the on-line state as soon as the driver gets any response from it. The device will then be normalised.

# General Driver description

## Cache

This driver is of the ‘Front-End-Back-End’ type, and therefore has a cache list of all 248 free configurable channels that exists in the device. Each channel consists of 16 bits data. Two consecutive channels form a 32-bit IEEE float. The size of the cache memory is about 1860 bytes per device. This is allocated from the linear 32-bit memory space.

The channel is valid as long as it is read by Citect within the CacheLiveTime (defaults to 30 seconds). If the time has expired, the value is actually read from the device to update the cahce list. If the tag is defined for Cache Reads (see below, no 'P' added to address) then the cache timer never expires.

This means that Citect indicates a very high channel usage, though the default is to handle 10 outstanding DCB’s at one time.

## Cyclic update vs. Cache reads

The device is read using two methods, the first method is to read the desired channel directly from the device, this is called Cyclic Update. The second method is to read the channel from the drivers' cache. This method is based upon the fact that the driver polles the devices' event queue to see if any channel change has occured. This is subject for confusion.

However, the desired method is the second (cache reads), because it will keep the communication on the SLPD bus at a reasonable level. Cyclic update has to poll every channel defined for this method directly from the device, which will cause the response to be slow. This is of course only true if the CacheLiveTime has expired for that channel (defaults to 30 s).

The read method is selected by using different addresses when the tags are defined, i.e. a 'P' as address suffix indicates that this channel is to be explicit polled (cyclic update). Ex IP4, or RP8.

## First time reads

When Citect starts and the Alarm Server begins to request values, a first explicit poll is made of the channels requested, even though they are defined as Cache Read tags. This is because the driver has no idea of the previous state of the channel. Once the first explicit poll is made, the normal event queue poll takes over, and the driver responds with values directly from the cache. This will cause the response to be poor immediately following a startup until the cache is filled.

## Request Performance

Due to the nature of the SLPD protocol, and the possibility to use Cyclic Update and Cache Reads, Citect automated blocked reads are turned off. Tests has shown that channel reads should be made for 16 channels per request to keep the performance as high as possible. The medium response time for such a request is about 0,1 seconds.

## SLPD Performance

The SLPD protocol has a fairly simple master slave structure, and communicates with the maximum speed of 9600 bps. This means that it has a generally bad performance when Cyclic Update is used.

## Writes

Write requests are never cached, they are performed at once. However, Citect may push a lot of write DCB’s at the same address if the user use a Slider etc to set the value, and let it use ‘Continous update of tag’. The driver could get a lot of consecutive write requests to the same address, and will handle them in the order they arrived.

If the variable that is to be written never has been read before and is of a digital type, it will be read, the value is saved in the cache and then normal processing take over, i.e. masking of the accurate bit, and rewriting.

## Citect Cache

Citect do not need to do any cache, it will be handled by the driver.

## System Device

The System device is a virtual device used to get the PDSW (PD Status Word), ISA, RSA, ISD, RSD and Program data, because Citect will reject requests to any device that is put off-line. The device is always off-line in programming mode. The System device is defined using the address ‘SYSTEM’.

## NOVATUNE.DBF

The Novatune specification for SLPD contains 15 different variables. The first one is explained:

TEMPLATE	UNIT_TYPE	RAW_TYPE	BIT WIDTH	LOW	HIGH	COMMENT

IP%U(0)%*256	0x0004	1	16	0	247	Integer, polled

This row describes the polled integer channel (uses Cyclic Update). The address of the channel is mulitplied by 256 to avoid Citect blocking. Blocking is made internally by the driver.

# User Interface

## Introduction

This section defines how the user will see the driver.  This relates directly to how the Citect forms need to be filled out and any special INI options.  For the kernel, the debug trace messages and the Stats.Special counters are documented.

## Driver Name

NOVATUNE

## Ports Form

### Baud Rate

9600 bps, or lower. The baudrate is set in the different devices.

### Data Bits

8

### Stop Bits

2

### Parity

Odd (observe that this is an full 8 bit protocol using even parity, not 7 bits)

### Special Options for serial comms

None

### Special Options for UDP

-iipaddress –pport –u

Example:

-i192.168.123.225 –p10001 –u

No settings are necessary for the Baud Rate, Data Bits, Stop Bits and Parity fields. They should be left blank.

## IO Devices Form

### Protocol

NOVATUNE

### Address

The address format looks like 241 etc. The address format is decimal and span from 1 to 254. One special address is used to maintain the bus, it is called SYSTEM. This 'virtual device' is described in a previous section.

## Pulldown lists Help

The following entries should be included in the Citect Help.DBF spec file.

| TYPE | DATA | FILTER |
| --- | --- | --- |
| PROTOCOL | NOVATUNE |  |

## IO Device Data Types and Formats

| IO Device Data Type | Valid Range | Citect Data Type | Description |
| --- | --- | --- | --- |
| Float | 3.4E +/- 38 | REAL | 7 digits |
| Integer | -32768 - +32767 | INT |  |
| Boolean | 0 – 1 | DIGITAL |  |
| Long | -2,147,483,648 - +2,147,483,647 | LONG |  |
| String |  | STRING | Is used for ISA, RSA, IPAR and PROGRAM variables. |

## IO Device Function Blocks and their Parameters (NOVATUNE.DBF)

| IO Device Type | Data type | Novatune Name |
| --- | --- | --- |
| IPx | Integer | Integer, polled. Reads/writes a channel of 16 bits. If the channel in the driver cache is valid (CacheLiveTime has not expired since last physical device read) then the cached value is returned. Otherwise, the channel is actually polled from the device. 16 channels are always read in one request. The other 15, none requested channels, are also inserted into the cache, and their CacheLiveTimer is updated. This variable is only valid at a physical device. |
| Ix | Integer | Integer, event. Reads/writes a channel of 16 bits. If the channel in the driver cache is valid (has been polled or updated by event queue reads at least once since the driver started) then the cached value is returned. Otherwise, the channel is actually polled from the device. 16 channels are always read in one request. The other 15, none requested channels, are also inserted into the cache, and their CacheLiveTimer is updated. This variable never causes the driver to do physical reads (unless first time). The channel is assumed to be updated by the event queue polls. This require that the device is programmed for that and is the fastest update method. It also causes the less bus traffic. This variable is only valid at a physical device. |
| IPx.y | Digital | Digtal bit, polled. Reads/writes a bit in a channel of 16 bits. If the channel in the driver cache is valid (CacheLiveTime has not expired since last physical device read) then the cached value is returned. Otherwise, the channel is actually polled from the device. 16 channels are always read in one request. The other 15, none requested channels, are also inserted into the cache, and their CacheLiveTimer is updated. If the first access to this variable is a write request, the driver first reads the channel before the masking. This variable is only valid at a physical device. |
| Ix.y | Digital | Digital bit, event. Reads/writes a bit in a channel of 16 bits. If the channel in the driver cache is valid (has been polled or updated by event queue reads at least once since the driver started) then the cached value is returned. Otherwise, the channel is actually polled from the device. 16 channels are always read in one request. The other 15, none requested channels, are also inserted into the cache, and their CacheLiveTimer is updated. This variable never causes the driver to do physical reads (unless first time). The channel is assumed to be updated by the event queue polls. This require that the device is programmed for that and is the fastest update method. It also causes the less bus traffic. If the first access to this variable is a write request, the driver first reads the channel before the masking. This variable is only valid at a physical device. |
| RPx | Real | Real, polled. Reads/writes two channels of 16 bits (32 bits). If the channel in the driver cache is valid (CacheLiveTime has not expired since last physical device read) then the cached value is returned. Otherwise, the channel is actually polled from the device. 16 channels are always read in one request. The other 15, none requested channels, are also inserted into the cache, and their CacheLiveTimer is updated. This variable is only valid at a physical device. |
| Rx | Real | Real, event. Reads/writes two channels of 16 bits (32 bits). If the channel in the driver cache is valid (has been polled or updated by event queue reads at least once since the driver started) then the cached value is returned. Otherwise, the channel is actually polled from the device. 16 channels are always read in one request. The other 15, none requested channels, are also inserted into the cache, and their CacheLiveTimer is updated. This variable never causes the driver to do physical reads (unless first time). The channel is assumed to be updated by the event queue polls. This require that the device is programmed for that and is the fastest update method. It also causes the less bus traffic. This variable is only valid at a physical device. |
| IPARa.b.c | String | Integer (byte) parameters. Reads/writes an array of parameters in an element. This request never uses the cache and is significally slow, though the devices seldom returns the parameters in one message if the array is large. The address could look like IPAR10.1.42, which means that element 1 of block 10 will be read/written with 42 parameters (this is the number of parameters that a TTAB contains). Actually, this causes the driver to issue two physical reads, because of the limited SLPD message length. The data is a string of decimal numbers, like '001007030' for 3 parameters, 1, 7 and 30. Each byte is always represented by three characters and, if neccessary, leading zeroes. This variable is only valid at a physical device. |
| IPARSa.b.c | String | Integer (byte) parameters. Reads/writes an array of parameters in an element. This request never uses the cache. The address could look like IPARS11.2.5, which means that element 2 of block 11 will be read/written with 5 parameters. The data is semicolon delimited string segments of data, like '1;7;3;5;5;’. When the variable is written, the string must not necessary contain all parameters. It is possible to write ‘2;7’ which means that the driver will write only IPAR 1 and IPAR 2 of element 2 in block 11. The driver will never write more parameters than defined (5 in the above example). This variable is only valid at a physical device. |
| RPARSa.b.c | String | Real parameters. Reads/writes an array of parameters in an element. This request never uses the cache. The address could look like RPARS11.2.5, which means that element 2 of block 11 will be read/written with 5 parameters. The data is semicolon delimited string segments of data, like '1.5;-1.5;0.08;2;3.2;’. When the variable is written, the string must not necessary contain all parameters. It is possible to write ‘2.2;7’ which means that the driver will write only RPAR 1 and RPAR 2 of element 2 in block 11. The driver will never write more parameters than defined (5 in the above example). This variable is only valid at a physical device. |
| ISA | String | Integer, System Wide Address. All integer parameters in the device is available using this address variable. It is set to the desired address, i.e. 241.10.1.1 for device 241, block 10, element 1, parameter 1. The parameter itself is physically read/written by the ISD variable, it never passes the cache. This variable is only valid at the virtual SYSTEM device. |
| ISD | Integer | Integer, System Wide Data. This variable is the parameter that the ISA address points to. When it is read/written it causes the driver to issue a physical request. The request never passes the cache. This variable is only valid at the virtual SYSTEM device. |
| RSA | String | Real, System Wide Address. All real parameters in the device is available using this address variable. It is set to the desired address, i.e. 241.9.1.2 for device 241, block 9, element 1, parameter 2. The parameter itself is physically read/written by the RSD variable, it never passes the cache. This variable is only valid at the virtual SYSTEM device. |
| RSD | Real | Real, System Wide Data. This variable is the parameter that the RSA address points to. When it is read/written it causes the driver to issue a physical request. The request never passes the cache. This variable is only valid at the virtual SYSTEM device. |
| MODEu | Integer | Mode (PDSW). Every device has a PDSW (PD Status Word) that indicates their state. This variable can enter five different states: 0 – Running, the device is in run mode. This is the default startup state, and this will be what the driver reports back to Citect even if there are no contact to the the device. 1 – Local, the device is connected to a PC through the local port and is in the local mode. 2 – Local Programming, the device is connected to a PC through the local port, and has entered the download mode. 3 – Remote programming, the device is downloaded using the SLPDUPDN program through Citect. 4 – Poll Off Line, the device has been taken out of the event queue poll sequence by setting mode to 4. 8 – Poll Off Line - Waiting for Citect Init, the device is on its way back from mode 4, but Citect hasn't made any new init yet. This is made every WatchTime which defaults to 30 seconds. The modes 0-3 are initiated by the device itself through the event queue. The other two modes are driver modes and are entered only by Citect or user requests. When the device change mode it will place a message in its event queue, and the driver will read it. Modes 1-3 always results in a device off-line and requests from any picture etc will be rejected with the #COM result. However, the device will still be event queue polled. If this variable is written, the only valid data is 0 (Running) or 4 (Poll Off Line), any other value than 0 or 4 will always be treated as a 4 (Poll Off Line). Mode 4 (Poll Off Line) will delete the device from the event queue poll chain, and put it off-line reporting back mode 4. This will cause the driver to totally ignore the device, no requests whatsoever will be sent to it, not even event queue polls and this will give the off line #COM result. To insert the device into the event queue again, the mode variable must be set to 0 (Running). This will put it back into the event queue poll chain, and it will enter mode 8 until Citect has made its next unit init (within WatchTime), during this time the device will still be off line. When Citect makes its unit init request to this device, the driver will do a normalise and a PDSW read that will read the physical device mode if the device is available. This will be reflected back in the mode variable changing to 0-3 depending of the PDSW. This function is valuable if the device should be shut down manually, because the driver will not have to wait for timeout as it would if the device simply is disconnected or turned off. Mode 0 doesn't necessary indicate that the device is healty and on line, though the device off/online mechanism depend of not only the device PDSW. If there are no contact with the device, the mode will never change, but it will go off line when 6 consecutive event queue polls with no answer is made. Alternatively if a Citect requests a value from this device, one question and two retries with no answer will result in an offline state. The mode variable will still be reporting the last read PDSW, which uses to be 0 (Running). To check for off lines, the Cicode IODeviceState() function should be used. This variable is valid both at the virtual SYSTEM device and any physically device. The u number indicates which physical device it actually points to. The SYSTEM device should be used, because it will never go off-line causing Citect to reject requests to the mode variable. Otherwise it would be possible to set the device manually Poll Off Line (4) and never be able to re-enable it by set the variable to 0 (Running) because Citect will reject all writes to a device that is off line. |
| SYSMSGu | Long | System Messages. When the event queue is polled from the devices, it sometimes respond with system messages, not only channel changes. The system messages indicates if the device is rebooted, has changed mode, has an error etc (described in the SLPD description). These messages are saved in a driver internal queue of 32 messages per device and are popped from this queue when this variable is read until the queue is empty. When the queue is empty, the driver returns the value 0. This way Citect may check if the device actually has rebooted, and then write back any lost set point values instead of writing the set point values everytime Citect is started. This variable is valid both at the virtual SYSTEM device and any physically device. The u number indicates which physical device it actually points to. It is preferred to use the SYSTEM device, because it will never go off-line, causing Citect to reject requests to SYSMSG. |
| SYSMSGu.n | Digital | This is a System Message array. Every system message has a digital connected to it. This digital will be set if a corresponding system message is received. This allows the system messages to be defined as tags and thereby alarm tags. When a system message is received the digital is set. When it is read it will reset, but the reset action is delayed by the SysMsgDelay parameter (defaults to 5000 ms). The system message number (n) is described in the SLPD description and corresponds to the D4 byte in decimal. I.e 0 = Restart, 17 (11 hex) = Mode Change, 20 (14 hex) = Bad parameter address etc. Observe that this number is in decimal and not hex as in the SLPD manual. This variable is valid both at the virtual SYSTEM device and any physically device. The u number indicates which physical device it actually points to. It is preferred to use the SYSTEM device, because it will never go off-line, causing Citect to reject requests to SYSMSG. |
| SETP | Integer | Set Parameter to RWM. When the ISD, RSD or IPAR has been used to write any new parameters to the device, it only writes to the EEPROM memory due to the nature of the SLPD protocol. To transfer the changes to the RAM (RWM) SETP has to be used. This variable may not be read and the address of the device that should have SETP sent to it is simply written to the variable, i.e. SETP=241. This variable is only valid at the virtual SYSTEM device. If the value 0 is written to this variable, it will automatically send a SETP to the last device that was written using any ISD/RSD or IPAR variable. This is only true if no SETP has been sent since the last ISD/RSD/IPAR write to avoid mutlitple writes if a push button is defined that sets SETP to 0 for more than one channel. |
| PROGRAM | String | Program pipe. To up- and download a program to any device this variable is used. The up-/download program use CTAPI functions (ctTagRead/ctTagWrite) to accomplish this. When this variable is read, the first three positions of the returned string is the length of the data (if any returned) in decimal format and the rest of the string is the data returned from the device, i.e. ”006225000007230000” is a 6 byte answer to a request. When this variable is written, it will use a similar format. The length is not icluded. Ex. ”225000035” is a command to the 225 device, using a data field of 000 bytes. This variable is only valid at the virtual SYSTEM device. The up-/donwload program may use a TCP socket connecting directly to the driver DLL to avoid ctAPI calls, in this configuration the PROGRAM tag is not needed. |
| ONLINE | Integer | Returns the number of devices that has the on line status set. |

Where:

| x y a b c u n | Channel number, 0 to 248. Bit number, 0-15. Block number, 0-255. Element number, depends of the program. Parameter numbers, depends of the program. Unit number (physical device number), 1-254. System Message number (0-31) |
| --- | --- |

## PROTDIR.DBF

| TAG | FILE | BIT_BLOCK | MAX_LENGTH | OPTIONS |
| --- | --- | --- | --- | --- |
| NOVATUNE | NOVATUNE | 16 | 256 | 0x04f |

## Parameters and INI options

### Standard Parameters

Block		1	(Citect blocking is always prohibited)

Delay		750 ms

MaxPending 	10

Polltime		0 ms	(interrupt driven)

Timeout	2000 ms

Retry		2

WatchTime	30 s

### Driver Specific Parameters

All Novatune specific parameters are located in the section ‘Novatune'

| PARAMETER | DEFAULT | DESCRIPTION |
| --- | --- | --- |
| CacheLiveTime | 30000 (ms) | The time a channel should be considered valid in the cache before it is marked as invalid. If the channel is marked invalid, then it will automatically be re-read the next time Citect asks for it. The elapsed time since the last read is calculated every time Citect asks for one channel. Every channel has its own timer. Only Cyclic Updated channels (defined with a tag address suffixed by 'P') are affected by the CacheLiveTime. |
| CacheCleanTime | 300000 (ms) | The time that elapses between cache cleaning. When this timer expires, the driver scans through all channel timers in the cache and marks old ones (>CacheLiveTime) as invalid. Global RTC broadcasts are handled when this time has elapsed, which means that if a interval is used to set the RTC, it will not be set until next expiration of CacheCleanTime. |
| MaxPollDelay | 4000 (ms) | Max interval that is allowed between two event queue polls. If there are lots of tags that are polled (i.e. 'P' suffix), the normal event queue polls will suffer. To be sure that no events are lost, this time indicates the maximum time that will be allowed for Cyclic Updates before the event queue is polled. |
| TurnOffPoll | 0 | If set to 1, it will turn off event queue polls. Valuable when debugging any communication. |
| SysMsgDelay | 5000 (ms) | The time incoming system message should be in its active state when it has been read before they are reset. This is valid only for the System Message array. |
| ClearCacheAtInit | 1 | When any device reboots it creates a system event. If the driver finds such event it usually flushes the cache (all channels marked invalid) to force itself to re-read any values. During the boot time any events are lost and this prevents it. |
| ClearCacheAt- ModeChange | 1 | When any device changes mode (from Local Program to Normal etc) it creates a system event. If the driver finds such event it usually flushes the cache (all channels marked invalid) to force itself to re-read any values. |
| ClearRXBufferOnSend | 1 | Indicates wheter the driver should clear any characters in the receive buffer before it transmits any new message. |
| ClearCacheAt- EventFull | 1 | If the event queue is filled (could be caused by many fast changes at the digital inputs) the devices creates a system event, indicating that it has lost events. If the driver finds such event it usually flushes the cache (all channels marked invalid) to force itself to re-read any values. |
| AutoEvent | 1 | If set to 1, and the driver receives updates of channels during normal event queue polls it marks the channel as Cache Read. Even if the tag is defined as Cyclic Update (tag address suffix 'P') it won't cause the driver to actually read the channel, because it has already been updated and will in the future be updated by normal event polls. |
| RejectedPolls- BeforeOffLine | 6 | The number of event queue polls that the device do not respond to before it is put off-line. If the mode changes is not 0 (Running) the device is always immediately put off-line. |
| BreakTime | xx (ms) | The break time. Defaults to 40 bits, or 33 ms if Citect reports no baud rate. |
| PauseTime | xx (ms) | The pause time. Defaults to 40 bits, or 33 ms if Citect reports no baud rate. |
| GlobalRTCSet | 02:30:00 00:30 | The time when the RTC update broadcast will be sent. If set to an invalid time (>23:59:59), no RTC update broadcasts will be sent. If this parameter is entered using a HH:MM format, i.e. 00:30, a interval is used instead of a time of day. The time expirations are checked when the cache is cleaned, which means that the broadcasts will differ somewhat from the time desired. |
| SetRTCAtInit | 0 | If set to 1, it will cause the driver to send out a time update broadcast before any devices are set on line. Any time update broadcast consists of three subsequent RTC broadcasts. |
| AlignBlockReads | 0 | If set to 1, it will cause all reads to begin at an even block boundary. The default is 16 channel reads in one message. I.e. it will cause a read from channel 3 to read channel 0-15 instead of 3-18 which is default. If the channel that is desired is on a boundary limit, the boundary is moved one channel, i.e. if channel 15 is to be read, channel 1-16 (not 0-15) will be read. This is bacause of the real format that will need 32 bits (two channels). |
| AllowSystemPollDisable | 0 | If set to 1, it will cause the driver to report all devices off line if no system device exist at that channel. This is true if the system device never has been created in the device database or if it has not been initialized by the driver. This will cause the IODeviceControl() function (if applied to the system device) to stop all communication at that channel and thus returning off line status for all devices. |
| StartupOffLineTime | 0 (ms) | If set, it will cause the driver to report all devices off line until this time has expired. This is valuable if redundancy with shared ports are used and some CiCode should have time to be executed at the startup sequence. The CiCode should determine if this server would do any communications. If not, there will then be enough time to disable the system device using the IODeviceControl() function and thus prevent any communication from this server that could corrupt the primary server communication. This parameter should only be used at the standby server. |
| ShowTraceInHex | 0 | If set to 1, it will change the Citect default trace format (decimal/hex mixed) to only hex with two characters per byte and a space between, i.e 00 FE 07 19 A3 00. |
| ShowTrace- DataOnly | 0 | If set to 1, it will cause the debug function to show only poll messages that caused response with data. All other messages will be shown as usual. This will significally decrease the amount of debug information that is show, though most information is normal polls without returned data. The number of hidden empty messages is showed in the header. |
| ShowTrace-Extended | 0 | If set to 1, it will cause all DCB requests from Citect to be output in the Kernel window. All replies from the driver will also be shown (compare to 'probe') with a lot of debugging information. Be careful using this debug method, though it will decrease performance of the driver. |
| NormaliseAllChannels | 0 | If set to 1, it will cause the normalise sequence to send FF FF as channel data. This will cause the event queue to be cleared. |
| SetRTCAtNormalise | 1 | If set to 0, it will cause the driver to not set the device clock at startup. If this parameter is 1 and the SetRTCAtInit is set to 1, the first normalise will not set the clock, though it will be set by a clock broadcast when the CacheCleanTime expires the first time. |
| DebugOnlyThisDevice | 0 | If set, it will cause the debugger function in Kernel to only reflect messages to and from this device. The devices' physical number should be entered (i.e. 1-254). Error messages will always be reflected in Kernel from all devices (if debugging is turned on). |
| ForceAllPolled | 0 | If set to 1, it will cause the driver to explicity poll all requested DCBs using the normal driver cache algorithm. Even if the event queue is polled, the values will be regarded as invalid and they will be polled instead. This will significally degrade performance. To be able to use this for debugging purposes, the Alarms and Trend Server must be shut off in the Computer Setup (CITECT.INI). |
| ReturnEventVariablesAtOnce | 0 | If set to 1, it will cause the driver to return all cached event based valid values (I and R) at once already in the AppendDCB() function. This will significally speed up response if these values are read one by one using TagRead() etc. |
| SetPDelayTime | 0 (ms) | The time the driver will wait from a parameter is physically written until a SETP is issued, even if the SETP already is placed in the write queue. This will be done only if the adress used is 0. If this parameter including the parameter write time passes the watchtime, it could cause the ‘Driver not responding error’. |
| ProgramPort | 0 | The up-/download program may use TCP/IP instead of ctAPI (and the PROGRAM tag) to send and receive programs to the DSS. It will then connect directly to a socket in the driver. Default for the up-/download program is 14666. If set to 0, the program socket will be disabled. Range is 1-65535. Avoid use of ports below 1000. |
| ChannelControlFile |  | ChannelControlFile controls if Ports are online/offline. A separate thread in Novatune.DLL reads and erases this file each second. It is a text file and the complete path should be entered, ex: ChannelControlFile=C:\CitectSCADA\Data\IOControl.txt The should contain portname and its preferred status, ex: Port_SNT121_R=0 Port_SNT131_R=0 will set both ports offline and stop polling. Ex: Port_SNT121_R=1 Port_SNT131_R=1 Will set both ports (and all its devices) online There is a Driver Statistics variable (Channel Status) which reflects the port status |

## Driver Specific Errors

| Driver Error Code | Mapped to (Generic Error label) | Meaning of Error Code |
| --- | --- | --- |

## Driver Error Help

The following entries should be included in the Citect ProtErr.DBF spec file.

| PROTOCOL | MASK | ERROR | MESSAGE | REFERENCE | ACTION | COMMENT |
| --- | --- | --- | --- | --- | --- | --- |

## Debug Messages

Shows the outgoing/incoming data packets in hex. If error report level is set to ERROR the driver will report errors, i.e. if any erronous packets are received.

## Stats Special Counters

| Number | Label | Purpose/Meaning of this counter |
| --- | --- | --- |
| 0 | DCB Requests | Number of DCB requests (accumulated). |
| 1 | Inbuffer max | Maximum used bytes in the input buffer for the CPU service function (before they have been handled by the packet receive routine). |
| 2 | Invalid packets | Packets received that was not valid (bad LRC, invalid length etc). |
| 3 | Packets received | Total number of received packets. |
| 4 | Cache hits | Number of DCB’s that has been read directly from the Cache (did not cause a physical read). |
| 5 | Cache hit rate (%) | The hit rate (Cache hits / DCB Requests x 100). |
| 6 | Sent SLPD packets | Number of sent packets. |
| 7 | Resent packets | Resents packets caused by timeout. |
| 8 | Event Queue Polls | Number of packets that was normal event queue poll packets. |
| 9 | Answer Later | The number of times the devices reject subsequent packet reads. I.e. if a TTAB etc is read, it will cause two physical reads because the message length exceed the SLPD max limit. When the driver requests the second packet (or even the first in some cases) the device is not ready to answer at once, it then will return the ‘Answer Later’ message. The driver will the retry until it succeed. Three subsequent ‘Answer Later’ messages are considered to be a failure. |
| 10 | n/a |  |
| 11 | Outstanding DCB's | The momentary value of outstanding DCB’s that is serviced by the driver (default max is 10). |
| 12 | Max outst. DCB's | The top value of DCB’s that has been requested by Citect to be serviced by the driver. |
| 13 | Phys. read time (ms) | The time SLPD consumed to service the last request. |
| 14 | Cache Cleared | The number of times the driver found a event queue system message that caused it to clear the devices’ cache. These messages are ‘Restart’, ‘Event Queue Full’ and ‘Mode Change’. These defaults are changeable using the Novatune DLL options in CITECT.INI |
| 15 | Bad Event Data | If a incoming SLPD packet had correct LRC and preambles/postambles, but had bad data field, it will increase this statistic field. |
| 16 | Didn’t send packet | Packets not sent due to StartupOffLineTime or disabled System I/O Devices or disbled by ChannelControlFile control will increase this counter (instead of actually sending the packet) |
| 17 | Event Queue Normal | Normalises made of channel 0xfa (event queue full fixups) |
| 18 | Rejected polls | Indicates rejected polls (when PLC is online) |
| 19 | Channel status | Indicates channel status. 0 – The channel is set offline (using IODeviceControl() at System device etc). 1 – Channel is online 2 – Channel is disabled by the StartupOffLineTime timer |

## Program up/download

### Installation

The program is installed from two diskettes using the SETUP program. It will install itself into C:\Program\SlpdUpdn directory and create a shortcut in the start menu.

It is possible to install this program at a Citect client station, it does not need to be installed at an IOServer.

Observe that the program must NOT be used by more than one user at a time, otherwise packets will be mixed and the program files will be corrupt. The program verifies that it receivs the expected packet (up til 255 packets) to prevent this type of problem. If the packets are indicated to be out of sync then the uploaded file(s) should be deleted.

### Communication using ctAPI

Using ctAPI the program up line copy and down line load is made using the PROGRAM variable that is defined for each channel at the SYSTEM device. This variable is read and written using an external program through the ctAPI functions TagWrite and TagRead.

Due to the stack useage by ctAPI the access is made through a small C-stub called ctAPIx.EXE that serves as a out-of-process COM-server to the higher level VB program that do the actually program up and download.

The ctAPIx.EXE will be started and ended automatically by SLPDUPDN when its class object is created/deleted. The ctAPIx.EXE assumes that the CITECT\BIN directory is accessible from any of the system path settings (either in the System Settings in Windows NT/2000 or in the PATH environment variable in AUTOEXEC.BAT file)

### Communication using TCP/IP

Using TCP/IP the program up line copy and down line load is made using a TCP socket connection, where the SLPDUPDN program act as a socket client and the Novatune driver DLL conatins the socket server. To enable this connection the Citect.INI parameter ProgramPort must be set.

Communications method TCP/IP is selected in the SLPDUPDN.INI file by setting the ConnectionMethod parameter to 1. It defaults to 0 which means ctAPI calls.

The driver will create a server socket thread for the first port (channel) that is defined. This thread will handle all traffic no matter of the devices are located at that port or another port.
Hence the devices must have unique  physical addresses. The driver socket may only handle one active SLPDUPDN program. The SLPDUPDN program will open the port when it actually is doing some up- or download.

### Program layout

All devices that should be up/downloaded must be defined in the SLPDUPDN.INI file to reflect were they are located and to set the default directory and the SYSTEM device defined PROGRAM variable that should be used.

SLPDUPDN.EXE only has four different functions.

The Up Line Copy function could be made for several devices in serial, by simply selecting them in the list and select Up Line Copy. During the Up Line Copy function the device still runs without interruption.

The Down Line Load function is valid if only one device is selected. During the Down Line Load, the device will be set in the Remote Programming Mode (which is readable from the Mode variable at the SYSTEM device) and will cause the device to go offline during the download phase. If the device received the program properly it will compile it and restart, then returning to the Run mode.

The Copy function requires that two devices are selected, and will simply do a Up Line Copy of one device and a Down Line Load to the other device.

Every of these functions consumes several minutes to complete. The time is directly proportional to the program size. The number of transferred messages will be shown in the info row at the bottom.

The last function, opens a log file (named LOGFILE.TXT) in the directory where the selected devices' program files are located. The log file is opened using a standard editing tool, i.e. NOTEPAD.EXE.

The SLPDUPDN.INI file may look something like this:

[General]
; EditorAppl=c:\windows\tillbe~1\wordpad.exe
; ServerPrimary=\\IOServ1
; ServerSecondary=\\IOServ2

;
; Desired method to communicate with the Novatune driver
;
; 0 = ctAPI using the DCOM ctAPIx out-of-process object
; 1 = TCP/IP directly to the Novatune driver DLL (does not require access to ctAPI)
;
; Method 1 require that the Novatune.DLL driver is version 01.12 or later
;
ConnectionMethod=1

[DCOM]
ServerPrimary=LOCP75
ServerSecondary=LOCP77

[TCP]
ServerPrimary=127.0.0.1:14666
;ServerSecondary=

[DUCar]
002=PROGRAM_SLINGA_01,TA0220 Plan 6 Fläktrum 4130
222=PROGRAM_SLINGA_02,TA0230 Plan 7 Fläktrum 4132,c:\slask\mina dokument
225=PROGRAM_SLINGA_02,TA0231 Plan 7 Fläktrum 4132,+\duc225
252=PROGRAM_SLINGA_03,TA0420 Plan 1 Fläktrum 1162

The EditorAppl points to the editor that should be used to open the log file. If no editor is entered, NOTEPAD.EXE will be used.

The [DCOM] primary and secondary server are the DCOM remote servers (if a remote ctAPIx object is used).

The [TCP] primary and secondary server are the I/O servers (if TCP is used). The port number must be included.

Section DUCar has the following meaning (second row example):

225	The physical device number (the address of the device, range 1-254)

PROGRAM_SLINGA_02	The variable that is defined using the PROGRAM address at the SYSTEM device for the channel the device if physically located.

TA0231....	Descriptive text that appears in the program. This will make it easier for the user to select the correct device.

+\duc225	The path to were the program files should be written or read. If this is preceeded by a '+' then it will act as an addon to the path set in the command line for this program. In the latter example the fully path will be '\\ioserv\programs\duc225'. If no path is entered the default will be used. It uses to be 'My Documents'.

Even though it is possible for the driver to handle the same physical device number at different ports this program coud not!

The program also handles some command line options, i.e

c:\Program\SlpdUpdn\SlpdUpdn.EXE /d:225 /i:\\ioserv\slpd /p:\\ioserv\programs

where

/d:	If a device should be selected by default, this should be its physical address.

/i:	The SLPDUPDN.INI file is by default located in the same directory as the program itself. By using this option it may be put somewhere else. In this example the fully path will expand to '\\ioserv\slpd\slpdupdn.ini'.

/p:	If there should be a prefix to the path entered to each device in the INI file. The prefix is only used if the path in the INI file is preceeded by a '+'.

/f	Indicates that the suggested program name (Up Line Copy) should be of the format DUCxxx_yymmdd.BIN instead of the normal pppp_DUCxxx.BIN, where pppp is the variable that is defined with the PROGRAM address for this devices’ channel, xxx is the physical device number and yymmdd is the actual date, i.e 991017 etc.

/s:	Desired server. If DCOM is used for the CTAPIx object, the remote server may be given if the default server (set up by DCOMCNFG) is not to be used. Ex. \\IOServ1.

The programs that are up/downloaded are saved in a text file, and may be edited by Notepad if they should contain information about versions, ex

;
; SLPD Program Up-Line load started 06-15-1999 14:42:38
;
;
; Program uploaded 06-15-1999 14:42:48
;
#PROGRAM
038225004127002225000017017000001000006000001050000000000000000000000000000000000000000000000000000000000000077000
038225004127002225001000000000000000000000000000000048017000015000000000015000000225255255255255255255255255184000
038225004127002225002255255255255255255255255255255255255255255255255255255255001000000065065065065065255255196000
032225004102002225003255255136108001000001007000050000005255000000000017005001005007001000094000
#END
;
; Program Up-Line load ended 06-15-1999 14:42:48
;
; Elapsed time : 0 min, 10 sec
;

The area between the #PROGRAM and #END must not be changed, but in the header any information may be entered.

## Hints and Tips

It is strongly recommended to only use Cache Read variables. Cyclic Update will significally degrade performance of the driver, because it cause the driver to poll every channel.

However, this requieres the device to be programmed using the blocks that places updated channel data in the event queue (SLODZ etc).

MaxPending should be tested out. An appropriate value for a plant using only Cache Reads would be about 50-60, a mixed plant should have max 20-30 outstanding DCBs. The Kernel should never respond 'Driver not responding', this indicates a too high MaxPending value.

Increase the number of ports and decrease number of devices per line. This could be achieved either by multiple RS-422 lines using Digi or similar serial port equipment.
Another way to achieve this is to use Westermo ED-10 (SLPD specific version) and UDP to a local collection of devices.

# Basic Testing

## Introduction

The programmer will perform a minimum level of testing which is outlined here.

A sample Project is available which can be used as a starting point for the programmers test Project. When the programmer has completed basic testing and debugging this Project should by backed up and supplied to the Citect Testing department.

## Procedure

The following are points should be covered by basic testing.

- On startup the IO Device comes online without errors.

- OK

- The driver supports IO Devices of addresses as documented in the specification.

- OK

- The driver reports the IO Device offline when the IO Device is a) powered down, b) disconnected.

- OK

- The driver will re-establish communication with the IO Device after a) power cycle, b) disconnection/ reconnection.

- OK.

- Confirm that retries (if supported) and error reporting operate correctly.

- OK (Statistics report)

- The driver reads all the device data types documented as readable in this specification.

- OK

- The driver writes to all the device data types documented as writeable in this specification.

- OK

- The  driver reads and writes all data formats supported by the protocol, ie DIGITAL, INT, LONG, REAL, STRING.

- OK

- Test the limit of the IO Devices request size, this should be done for at least DIGITAL and an INT data formats.

- Not applicable to this driver.

- Let the driver run over night and check that no retries or other errors have occurred.

- OK

- If a multidrop or network protocol and if the hardware is available then the protocol should be tested with more than one IO Device connected.

– OK (12 devices tested)

# Performance Testing

## Introduction

Tests which give some indication of the drivers performance. The programmer needs to perform these tests since the results feed back into the Constants  structure and the PROTDIR.DBF.

## Calculating the Blocking Constant – Not applicable

Because this driver is of the ‘Front-End-Back-End’ type, and due to the nature of the SLPD protocol, it does not support Citect blocking. The channel read always read 16 channels, wich is just about the maximum for one request. This has been tested and found to be the fastest way to get required data from the device.

# References

## References

The fully protocol description is found in the IL-SPEC-7159/0, document 5766 398-19, available from ABB Automation.